{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["变量dat文件","CSpreadSheetBackup"],"not_rendered":{"external_links":1,"defined_names":2},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":33,"n_cols":76,"rows_kept":33,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","6.20.180.1","FS32N_1_SwitchCondition","开关机状态","4","2","1","3","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","16","180",null,null,"0","3","3",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["4","6.20.180.1","FS32N_1_RemoteControlSwitch","远控开/关状态","4","2","1","3","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","19","180",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["5","6.20.180.1","FS32N_1_RoomTemperature","房间温度","4","2","1","3","1",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","0.1","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["6","6.20.180.1","FS32N_1_RoomHumidity","房间湿度","4","2","1","3","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","0.1","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["7","6.20.180.1","FS32N_1_TemperatureSeting","温度设定","4","2","1","3","3",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","℃","300","0.1","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["8","6.20.180.1","FS32N_1_HumiditySeting","湿度设定","4","2","1","3","4",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","%","300","0.1","3","0","1","1","0","0","0","0","180",null,null,"0","0","0",{"$nulls":10},"0","0","100","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0"]
["11","6.20.180.1","FS32N_1_Alarm_BlowerOverLoad","送风机过载","4","2","1","3","7",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","16","180",null,null,"0","15","15",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","故障,"]
["12","6.20.180.1","FS32N_1_Alarm_AirPerssureFault","风压故障","4","2","1","3","7",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","17","180",null,null,"0","14","14",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","故障,"]
["13","6.20.180.1","FS32N_1_Alarm_Comp2HigPreProt","压缩机2高压","4","2","1","3","7",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","18","180",null,null,"0","13","13",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","故障,"]
["14","6.20.180.1","FS32N_1_Alarm_Comp1HigPreProt","压缩机1高压","4","2","1","3","7",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","19","180",null,null,"0","12","12",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","故障,"]
["15","6.20.180.1","FS32N_1_Alarm_Comp1LowPreProt","压缩机1低压","4","2","1","3","7",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","20","180",null,null,"0","11","11",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","故障,"]
["16","6.20.180.1","FS32N_1_Alarm_CondenserFan1OverLoad","冷凝风机1故障","4","2","1","3","7",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","21","180",null,null,"0","10","10",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","故障,"]
["17","6.20.180.1","FS32N_1_Alarm_HighTemperature","机温过高","4","2","1","3","7",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","22","180",null,null,"0","9","9",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","故障,"]
["20","6.20.180.1","FS32N_1_Alarm_FloorWaterAlarm","地板积水报警","4","2","1","3","7",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","25","180",null,null,"0","5","5",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","故障,"]
["21","6.20.180.1","FS32N_1_Alarm_FilterCloggingAlarm","过滤网堵塞报警","4","2","1","3","7",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","26","180",null,null,"0","4","4",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","故障,"]
["23","6.20.180.1","FS32N_1_Alarm_HigHumidLevelProt","加湿高水位","4","2","1","3","7",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","28","180",null,null,"0","3","3",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","故障,"]
["24","6.20.180.1","FS32N_1_Alarm_WettingCurrentOverrunProte","加湿电流超限","4","2","1","3","7",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","29","180",null,null,"0","2","2",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","故障,"]
["25","6.20.180.1","FS32N_1_Alarm_Comp2LowPreProt","压缩机2低压","4","2","1","3","7",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","30","180",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","故障,"]
["26","6.20.180.1","FS32N_1_Alarm_CondenserFan2OverLoad","冷凝风机2故障","4","2","1","3","7",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","31","180",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","故障,"]
["11","6.20.180.1","FS32N_1_Output_BlowerControl","送风机控制","4","2","1","3","9",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","16","180",null,null,"0","15","15",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","故障,"]
["12","6.20.180.1","FS32N_1_Output_Compressor1Control","压缩机1控制","4","2","1","3","9",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","17","180",null,null,"0","14","14",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","故障,"]
["13","6.20.180.1","FS32N_1_Output_CondenserFan1Control","冷凝风机1控制","4","2","1","3","9",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","18","180",null,null,"0","13","13",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","故障,"]
["14","6.20.180.1","FS32N_1_Output_ForValue1Control","供液阀1控制","4","2","1","3","9",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","19","180",null,null,"0","12","12",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","故障,"]
["15","6.20.180.1","FS32N_1_Output_Compressor2Control","压缩机2控制","4","2","1","3","9",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","20","180",null,null,"0","11","11",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","故障,"]
["16","6.20.180.1","FS32N_1_Output_CondenserFan2Control","冷凝风机2控制","4","2","1","3","9",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","21","180",null,null,"0","10","10",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","故障,"]
["17","6.20.180.1","FS32N_1_Output_ForValue2Control","供液阀2控制","4","2","1","3","9",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","22","180",null,null,"0","9","9",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","故障,"]
["18","6.20.180.1","FS32N_1_Output_Heat1Control","加热1控制","4","2","1","3","9",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","23","180",null,null,"0","8","8",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","故障,"]
["19","6.20.180.1","FS32N_1_Output_Heat2Control","加热2控制","4","2","1","3","9",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","24","180",null,null,"0","7","7",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","故障,"]
["21","6.20.180.1","FS32N_1_Output_HumidifierControl","加湿器控制","4","2","1","3","9",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","26","180",null,null,"0","5","5",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","故障,"]
["22","6.20.180.1","FS32N_1_Output_GeneralFaultOutput","总故障输出","4","2","1","3","9",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","27","180",null,null,"0","4","4",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","故障,"]
["24","6.20.180.1","FS32N_1_Output_HumidifierWaterSupplyControl","加湿器进水控制","4","2","1","3","9",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","29","180",null,null,"0","2","2",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","故障,"]
["25","6.20.180.1","FS32N_1_Output_HumidifierWaterDrainageControl","加湿器排水控制","4","2","1","3","9",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","30","180",null,null,"0","1","1",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","1","1,","故障,"]

{"sheet":"CSpreadSheetBackup","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}