{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["变量dat文件"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":554,"n_cols":76,"rows_kept":554,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","9.1.114.1","TEPW1_A_Phase","A_PhaseVoltageElectricityMeter","4","2","1","3","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","9.1.114.1","TEPW1_B_Phase","B_PhaseVoltageElectricityMeter","4","2","1","3","16",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","9.1.114.1","TEPW1_C_Phase","B_PhaseVoltageElectricityMeter","4","2","1","3","32",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","9.1.114.1","TEPW1_Aver_Phase","Electricity meter phase voltage","4","2","1","3","50",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","9.1.114.1","TEPW1_A_Curr","A three-phase power meter","4","2","1","3","4",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","A","900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","9.1.114.1","TEPW1_B_Curr","B three-phase power meter","4","2","1","3","20",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","A","900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","9.1.114.1","TEPW1_C_Curr","C three-phase power meter","4","2","1","3","36",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","A","900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","9.1.114.1","TEPW1_Aver_Curr","Electricity meter and current","4","2","1","3","52",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","A","900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","9.1.114.1","TEPW1_Freq","Electricity meter frequency","3","2","1","3","54",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","900","0.0010681300","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","9.1.114.1","TEPW1_AHavePower","Electricity meter A phase power dispatch","4","2","1","3","8",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","kw","900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","9.1.114.1","TEPW1_BHavePower","Electricity meter B phase power dispatch","4","2","1","3","24",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","kw","900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","9.1.114.1","TEPW1_CHavePower","Electricity meter C phase power dispatch","4","2","1","3","40",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","kw","900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","9.1.114.1","TEPW1_Aver_HavePower","Electricity meter in conjunction with the active power","4","2","1","3","56",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","kw","900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","9.1.114.1","TEPW1_A_Line","A line voltage electricity meter","4","2","1","3","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","9.1.114.1","TEPW1_B_Line","B line voltage electricity meter","4","2","1","3","18",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","9.1.114.1","TEPW1_C_Line","C line voltage electricity meter","4","2","1","3","34",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","9.1.114.2","TEPW2_A_Phase","A_PhaseVoltageElectricityMeter","4","2","1","3","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["18","9.1.114.2","TEPW2_B_Phase","B_PhaseVoltageElectricityMeter","4","2","1","3","16",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["19","9.1.114.2","TEPW2_C_Phase","B_PhaseVoltageElectricityMeter","4","2","1","3","32",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["20","9.1.114.2","TEPW2_Aver_Phase","Electricity meter phase voltage","4","2","1","3","50",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["21","9.1.114.2","TEPW2_A_Curr","A three-phase power meter","4","2","1","3","4",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","A","900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","9.1.114.2","TEPW2_B_Curr","B three-phase power meter","4","2","1","3","20",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","A","900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","9.1.114.2","TEPW2_C_Curr","C three-phase power meter","4","2","1","3","36",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","A","900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["24","9.1.114.2","TEPW2_Aver_Curr","Electricity meter and current","4","2","1","3","52",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","A","900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["25","9.1.114.2","TEPW2_Freq","Electricity meter frequency","3","2","1","3","54",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","900","0.0010681300","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["26","9.1.114.2","TEPW2_AHavePower","Electricity meter A phase power dispatch","4","2","1","3","8",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","kw","900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["27","9.1.114.2","TEPW2_BHavePower","Electricity meter B phase power dispatch","4","2","1","3","24",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","kw","900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["28","9.1.114.2","TEPW2_CHavePower","Electricity meter C phase power dispatch","4","2","1","3","40",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","kw","900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["29","9.1.114.2","TEPW2_Aver_HavePower","Electricity meter in conjunction with the active power","4","2","1","3","56",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","kw","900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["30","9.1.114.2","TEPW2_A_Line","A line voltage electricity meter","4","2","1","3","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["31","9.1.114.2","TEPW2_B_Line","B line voltage electricity meter","4","2","1","3","18",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["32","9.1.114.2","TEPW2_C_Line","C line voltage electricity meter","4","2","1","3","34",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["33","9.1.114.3","TEPW3_A_Phase","A_PhaseVoltageElectricityMeter","4","2","1","3","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["34","9.1.114.3","TEPW3_B_Phase","B_PhaseVoltageElectricityMeter","4","2","1","3","16",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["35","9.1.114.3","TEPW3_C_Phase","B_PhaseVoltageElectricityMeter","4","2","1","3","32",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["36","9.1.114.3","TEPW3_Aver_Phase","Electricity meter phase voltage","4","2","1","3","50",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["37","9.1.114.3","TEPW3_A_Curr","A three-phase power meter","4","2","1","3","4",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","A","900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["38","9.1.114.3","TEPW3_B_Curr","B three-phase power meter","4","2","1","3","20",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","A","900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["39","9.1.114.3","TEPW3_C_Curr","C three-phase power meter","4","2","1","3","36",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","A","900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["40","9.1.114.3","TEPW3_Aver_Curr","Electricity meter and current","4","2","1","3","52",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","A","900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["41","9.1.114.3","TEPW3_Freq","Electricity meter frequency","3","2","1","3","54",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","900","0.0010681300","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["42","9.1.114.3","TEPW3_AHavePower","Electricity meter A phase power dispatch","4","2","1","3","8",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","kw","900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["43","9.1.114.3","TEPW3_BHavePower","Electricity meter B phase power dispatch","4","2","1","3","24",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","kw","900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["44","9.1.114.3","TEPW3_CHavePower","Electricity meter C phase power dispatch","4","2","1","3","40",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","kw","900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["45","9.1.114.3","TEPW3_Aver_HavePower","Electricity meter in conjunction with the active power","4","2","1","3","56",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","kw","900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["46","9.1.114.3","TEPW3_A_Line","A line voltage electricity meter","4","2","1","3","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["47","9.1.114.3","TEPW3_B_Line","B line voltage electricity meter","4","2","1","3","18",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["48","9.1.114.3","TEPW3_C_Line","C line voltage electricity meter","4","2","1","3","34",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["49","9.1.114.4","TEPW4_A_Phase","A_PhaseVoltageElectricityMeter","4","2","1","3","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["50","9.1.114.4","TEPW4_B_Phase","B_PhaseVoltageElectricityMeter","4","2","1","3","16",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["51","9.1.114.4","TEPW4_C_Phase","B_PhaseVoltageElectricityMeter","4","2","1","3","32",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["52","9.1.114.4","TEPW4_Aver_Phase","Electricity meter phase voltage","4","2","1","3","50",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["53","9.1.114.4","TEPW4_A_Curr","A three-phase power meter","4","2","1","3","4",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","A","900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["54","9.1.114.4","TEPW4_B_Curr","B three-phase power meter","4","2","1","3","20",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","A","900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["55","9.1.114.4","TEPW4_C_Curr","C three-phase power meter","4","2","1","3","36",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","A","900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["56","9.1.114.4","TEPW4_Aver_Curr","Electricity meter and current","4","2","1","3","52",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","A","900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["57","9.1.114.4","TEPW4_Freq","Electricity meter frequency","3","2","1","3","54",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","900","0.0010681300","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["58","9.1.114.4","TEPW4_AHavePower","Electricity meter A phase power dispatch","4","2","1","3","8",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","kw","900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["59","9.1.114.4","TEPW4_BHavePower","Electricity meter B phase power dispatch","4","2","1","3","24",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","kw","900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["60","9.1.114.4","TEPW4_CHavePower","Electricity meter C phase power dispatch","4","2","1","3","40",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","kw","900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["61","9.1.114.4","TEPW4_Aver_HavePower","Electricity meter in conjunction with the active power","4","2","1","3","56",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","kw","900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["62","9.1.114.4","TEPW4_A_Line","A line voltage electricity meter","4","2","1","3","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["63","9.1.114.4","TEPW4_B_Line","B line voltage electricity meter","4","2","1","3","18",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["64","9.1.114.4","TEPW4_C_Line","C line voltage electricity meter","4","2","1","3","34",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["65","5.29.128.1","AKCP_1_Temp","Port 1 temperature","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.16.1.3.0","public","0","0","0","0","15","32","0","0","0","癈","300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0","0","0"]
["66","5.29.128.1","AKCP_1_Humidity","Port 1 humidity","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.17.1.3.0","public","0","0","0","0","20","85","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0","0","0"]
["67","5.29.128.1","AKCP_2_Temp","Port 2 temperature","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.16.1.3.1","public","0","0","0","0","15","32","0","0","0","癈","300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0","0","0"]
["68","5.29.128.1","AKCP_2_Humidity","Port 2 humidity","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.17.1.3.1","public","0","0","0","0","20","85","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0","0","0"]
["69","5.29.128.1","AKCP_3_Temp","Port 3 temperature","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.16.1.3.2","public","0","0","0","0","15","32","0","0","0","癈","300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0","0","0"]
["70","5.29.128.1","AKCP_3_Humidity","Port 3 humidity","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.17.1.3.2","public","0","0","0","0","20","85","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0","0","0"]
["71","5.29.128.1","AKCP_4_Temp","Port 4 temperature","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.16.1.3.3","public","0","0","0","0","15","32","0","0","0","癈","300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0","0","0"]
["72","5.29.128.1","AKCP_4_Humidity","Port 4 humidity","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.17.1.3.3","public","0","0","0","0","20","85","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0","0","0"]
["73","5.29.128.1","AKCP_5_Temp","Port 5 temperature","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.16.1.3.4","public","0","0","0","0","15","32","0","0","0","癈","300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0","0","0"]
["74","5.29.128.1","AKCP_5_Humidity","Port 5 humidity","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.17.1.3.4","public","0","0","0","0","20","85","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0","0","0"]
["75","5.29.128.1","AKCP_6_Temp","Port 6 temperature","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.16.1.3.5","public","0","0","0","0","15","32","0","0","0","癈","300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0","0","0"]
["76","5.29.128.1","AKCP_6_Humidity","Port 6 humidity","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.17.1.3.5","public","0","0","0","0","20","85","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0","0","0"]
["77","5.29.128.1","AKCP_7_Temp","Port 7 temperature","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.16.1.3.6","public","0","0","0","0","15","32","0","0","0","癈","300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0","0","0"]
["78","5.29.128.1","AKCP_7_Humidity","Port 7 humidity","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.17.1.3.6","public","0","0","0","0","20","85","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0","0","0"]
["79","5.29.128.1","AKCP_8_Temp","Port 8 temperature","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.16.1.3.7","public","0","0","0","0","15","32","0","0","0","癈","300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0","0","0"]
["80","5.29.128.1","AKCP_8_Humidity","Port 8 humidity","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.17.1.3.7","public","0","0","0","0","20","85","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0","0","0"]
["81","7.33.132.1","FG_ALS_1_Line_Leak","Water Leakage","4","2","1","3","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","m","300","1.0000000000","3","0","1","1","0","0","0","0","132",null,null,"0","0","0","FG_ALS_1_Line_LeakPos",{"$nulls":9},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","1","1,","alarm,"]
["82","7.33.132.1","FG_ALS_1_Line_CableCut","Cable Break Off","4","2","1","3","4",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","132",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["83","7.33.132.1","FG_ALS_1_Line_LeakPos","Leakage Location","4","2","1","3","6",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","m","300","1.0000000000","3","0","1","1","0","0","0","0","132",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["84","5.29.128.1","AKCP_Smoke","FM200","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.18.1.3.8","public","0","0","0","0","0","0","2","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","6,","Smoke Alarm,"]
["85","5.29.128.1","AKCP_Oil_Machine","Oil_Machine","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.18.1.3.9","public","0","0","0","0","0","0","2","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","6,","OilMachine Alarm,"]
["86","5.29.128.1","AKCP_Security","Security","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.18.1.3.10","public","0","0","0","0","0","0","2","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","6,","Security Alarm,"]
["87","4.11.18.1","UPS1_systemStatus","UPS1systemStatus","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.1.1.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.1000000015","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","2","2,","critical,"]
["88","4.11.18.1","UPS1_inletAirTemperature","inletAirTemperature","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.1.2.0","public","0","0","0","0","15","32","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["89","4.11.18.1","UPS1_dcBusVoltage","dcBusVoltage","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.1.3.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["90","4.11.18.1","UPS1_inputLineVoltageA","inputLineVoltageA","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.1.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["91","4.11.18.1","UPS1_inputLineVoltageB","inputLineVoltageB","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.2.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["92","4.11.18.1","UPS1_inputLineVoltageC","inputLineVoltageC","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.3.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["93","4.11.18.1","UPS1_inputPhaseVoltageA","inputPhaseVoltageA","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.4.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["94","4.11.18.1","UPS1_inputPhaseVoltageB","inputPhaseVoltageB","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.5.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["95","4.11.18.1","UPS1_inputPhaseVoltageC","inputPhaseVoltageC","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.6.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["96","4.11.18.1","UPS1_inputCurrentA","inputCurrentA","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.7.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["97","4.11.18.1","UPS1_inputCurrentB","inputCurrentB","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.8.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["98","4.11.18.1","UPS1_inputCurrentC","inputCurrentC","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.9.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["99","4.11.18.1","UPS1_inputFrequency","inputFrequency","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.10.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["100","4.11.18.1","UPS1_bypassPhaseVoltageA","bypassPhaseVoltageA","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.3.1.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["101","4.11.18.1","UPS1_bypassPhaseVoltageB","bypassPhaseVoltageB","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.3.2.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["102","4.11.18.1","UPS1_bypassPhaseVoltageC","bypassPhaseVoltageC","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.3.3.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["103","4.11.18.1","UPS1_bypassFrequency","bypassFrequency","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.3.4.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["104","4.11.18.1","UPS1_outputPhaseVoltageA","outputPhaseVoltageA","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.1.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["105","4.11.18.1","UPS1_outputPhaseVoltageB","outputPhaseVoltageB","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.2.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["106","4.11.18.1","UPS1_outputPhaseVoltageC","outputPhaseVoltageC","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.3.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["107","4.11.18.1","UPS1_outputCurrentA","outputCurrentA","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.4.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["108","4.11.18.1","UPS1_outputCurrentB","outputCurrentB","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.5.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["109","4.11.18.1","UPS1_outputCurrentC","outputCurrentC","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.6.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["110","4.11.18.1","UPS1_outputFrequency","outputFrequency","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.7.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["111","4.11.18.1","UPS1_outputActivePowerA","outputActivePowerA","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.11.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["112","4.11.18.1","UPS1_outputActivePowerB","outputActivePowerB","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.12.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["113","4.11.18.1","UPS1_outputActivePowerC","outputActivePowerC","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.13.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["114","4.11.18.1","UPS1_outputApparentPowerA","outputApparentPowerA","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.14.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["115","4.11.18.1","UPS1_outputApparentPowerB","outputApparentPowerB","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.15.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["116","4.11.18.1","UPS1_outputApparentPowerC","outputApparentPowerC","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.16.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["117","4.11.18.1","UPS1_outputLoadA","outputLoadA","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.20.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["118","4.11.18.1","UPS1_outputLoadB","outputLoadB","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.21.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["119","4.11.18.1","UPS1_outputLoadC","outputLoadC","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.22.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["120","4.11.18.1","UPS1_batteryVoltage","batteryVoltage","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.5.1.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["121","4.11.18.1","UPS1_batteryCurrent","batteryCurrent","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.5.2.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["122","4.11.18.1","UPS1_batteryRemainsTime","batteryRemainsTime","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.5.3.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["123","4.11.18.1","UPS1_batteryTemperature","batteryTemperature","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.5.4.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["124","4.11.18.2","UPS2_systemStatus","UPS2systemStatus","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.1.1.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","2","2,","critical,"]
["125","4.11.18.2","UPS2_inletAirTemperature","inletAirTemperature","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.1.2.0","public","0","0","0","0","15","32","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["126","4.11.18.2","UPS2_dcBusVoltage","dcBusVoltage","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.1.3.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["127","4.11.18.2","UPS2_inputLineVoltageA","inputLineVoltageA","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.1.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["128","4.11.18.2","UPS2_inputLineVoltageB","inputLineVoltageB","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.2.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["129","4.11.18.2","UPS2_inputLineVoltageC","inputLineVoltageC","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.3.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["130","4.11.18.2","UPS2_inputPhaseVoltageA","inputPhaseVoltageA","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.4.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["131","4.11.18.2","UPS2_inputPhaseVoltageB","inputPhaseVoltageB","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.5.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["132","4.11.18.2","UPS2_inputPhaseVoltageC","inputPhaseVoltageC","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.6.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["133","4.11.18.2","UPS2_inputCurrentA","inputCurrentA","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.7.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["134","4.11.18.2","UPS2_inputCurrentB","inputCurrentB","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.8.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["135","4.11.18.2","UPS2_inputCurrentC","inputCurrentC","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.9.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["136","4.11.18.2","UPS2_inputFrequency","inputFrequency","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.10.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["137","4.11.18.2","UPS2_bypassPhaseVoltageA","bypassPhaseVoltageA","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.3.1.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["138","4.11.18.2","UPS2_bypassPhaseVoltageB","bypassPhaseVoltageB","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.3.2.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["139","4.11.18.2","UPS2_bypassPhaseVoltageC","bypassPhaseVoltageC","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.3.3.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["140","4.11.18.2","UPS2_bypassFrequency","bypassFrequency","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.3.4.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["141","4.11.18.2","UPS2_outputPhaseVoltageA","outputPhaseVoltageA","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.1.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["142","4.11.18.2","UPS2_outputPhaseVoltageB","outputPhaseVoltageB","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.2.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["143","4.11.18.2","UPS2_outputPhaseVoltageC","outputPhaseVoltageC","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.3.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["144","4.11.18.2","UPS2_outputCurrentA","outputCurrentA","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.4.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["145","4.11.18.2","UPS2_outputCurrentB","outputCurrentB","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.5.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["146","4.11.18.2","UPS2_outputCurrentC","outputCurrentC","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.6.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["147","4.11.18.2","UPS2_outputFrequency","outputFrequency","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.7.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["148","4.11.18.2","UPS2_outputActivePowerA","outputActivePowerA","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.11.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["149","4.11.18.2","UPS2_outputActivePowerB","outputActivePowerB","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.12.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["150","4.11.18.2","UPS2_outputActivePowerC","outputActivePowerC","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.13.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["151","4.11.18.2","UPS2_outputApparentPowerA","outputApparentPowerA","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.14.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["152","4.11.18.2","UPS2_outputApparentPowerB","outputApparentPowerB","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.15.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["153","4.11.18.2","UPS2_outputApparentPowerC","outputApparentPowerC","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.16.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["154","4.11.18.2","UPS2_outputLoadA","outputLoadA","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.20.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["155","4.11.18.2","UPS2_outputLoadB","outputLoadB","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.21.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["156","4.11.18.2","UPS2_outputLoadC","outputLoadC","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.22.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["157","4.11.18.2","UPS2_batteryVoltage","batteryVoltage","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.5.1.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["158","4.11.18.2","UPS2_batteryCurrent","batteryCurrent","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.5.2.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["159","4.11.18.2","UPS2_batteryRemainsTime","batteryRemainsTime","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.5.3.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["160","4.11.18.2","UPS2_batteryTemperature","batteryTemperature","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.5.4.0","public","0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["161","6.8.96.1","Air1_SystemOn","System On","4","2","1","1","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["162","6.8.96.1","Air1_Compressor_1","Compressor 1","4","2","1","1","3",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["163","6.8.96.1","Air1_Compressor_2","Compressor 2","4","2","1","1","4",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["164","6.8.96.1","Air1_Compressor_3","Compressor 3","4","2","1","1","5",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["165","6.8.96.1","Air1_Compressor_4","Compressor 4","4","2","1","1","6",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["166","6.8.96.1","Air1_El_Heater1","El. Heater 1","4","2","1","1","7",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["167","6.8.96.1","Air1_El_Heater2","El. Heater 2","4","2","1","1","8",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["168","6.8.96.1","Air1_Dehumidification","Dehumidification","4","2","1","1","11",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["169","6.8.96.1","Air1_Humidification","Humidification","4","2","1","1","12",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["170","6.8.96.1","Air1_HighRoomTemperatureAlarm","High Room Temperature","4","2","1","1","22",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air1_Alarm ,"]
["171","6.8.96.1","Air1_LowRoomTemperatureAlarm","Low Room Temperature","4","2","1","1","23",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air1_Alarm ,"]
["172","6.8.96.1","Air1_HighRoomHumidityAlarm","High Room Humidity","4","2","1","1","24",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air1_Alarm ,"]
["173","6.8.96.1","Air1_LowRoomHumidityAlarm","Low Room Humidity","4","2","1","1","25",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air1_Alarm ,"]
["174","6.8.96.1","Air1_CloggedFilterAlarm","Clogged Filter","4","2","1","1","27",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air1_Alarm ,"]
["175","6.8.96.1","Air1_LossofAirFlowAlarm","Loss of Air1 Flow","4","2","1","1","29",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["176","6.8.96.1","Air1_HeaterOverheatingAlarm","Heater Overheating","4","2","1","1","30",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air1_Alarm ,"]
["177","6.8.96.1","Air1_Circuit1HighPressureAlarm","Circuit 1 High Pressure","4","2","1","1","31",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air1_Alarm ,"]
["178","6.8.96.1","Air1_Circuit2HighPressureAlarm","Circuit 2 High Pressure","4","2","1","1","32",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air1_Alarm ,"]
["179","6.8.96.1","Air1_Circuit1LowPressureAlarm","Circuit 1 Low Pressure","4","2","1","1","33",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air1_Alarm ,"]
["180","6.8.96.1","Air1_Circuit2LowPressureAlarm","Circuit 2 Low Pressure","4","2","1","1","34",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air1_Alarm ,"]
["181","6.8.96.1","Air1_Humidifier_WaterLossAlarm","Humidifier: Water Loss","4","2","1","1","42",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air1_Alarm ,"]
["182","6.8.96.1","Air1_HumidifierGeneral Alarm","Humidifier General","4","2","1","1","66",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air1_Alarm ,"]
["183","6.8.96.1","Air1_UnitOnAlarm","Unit on","4","2","1","1","67",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air1_Alarm ,"]
["184","6.8.96.1","Air1_UnitON/OFFSwitch","Unit ON/OFF Switch","4","2","1","1","76",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air conditioning1 Unit1 Switch OFF ,"]
["185","6.8.96.1","Air1_RoomTemperature","Room Temperature","4","2","1","3","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["186","6.8.96.1","Air1_OutdoorTemperature","Outdoor Temperature","4","2","1","3","3",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["187","6.8.96.1","Air1_RoomRelativeHumidity","Room Relative Humidity","4","2","1","3","7",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["188","6.8.96.1","Air1_OutletChilledWaterTemperature","Outlet Chilled Water Temperature","4","2","1","3","8",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["189","6.8.96.2","Air2_SystemOn","System On","4","2","1","1","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["190","6.8.96.2","Air2_Compressor_1","Compressor 1","4","2","1","1","3",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["191","6.8.96.2","Air2_Compressor_2","Compressor 2","4","2","1","1","4",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["192","6.8.96.2","Air2_Compressor_3","Compressor 3","4","2","1","1","5",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["193","6.8.96.2","Air2_Compressor_4","Compressor 4","4","2","1","1","6",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["194","6.8.96.2","Air2_El_Heater1","El. Heater 1","4","2","1","1","7",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["195","6.8.96.2","Air2_El_Heater2","El. Heater 2","4","2","1","1","8",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["196","6.8.96.2","Air2_Dehumidification","Dehumidification","4","2","1","1","11",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["197","6.8.96.2","Air2_Humidification","Humidification","4","2","1","1","12",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["198","6.8.96.2","Air2_HighRoomTemperatureAlarm","High Room Temperature","4","2","1","1","22",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air2_Alarm ,"]
["199","6.8.96.2","Air2_LowRoomTemperatureAlarm","Low Room Temperature","4","2","1","1","23",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air2_Alarm ,"]
["200","6.8.96.2","Air2_HighRoomHumidityAlarm","High Room Humidity","4","2","1","1","24",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air2_Alarm ,"]
["201","6.8.96.2","Air2_LowRoomHumidityAlarm","Low Room Humidity","4","2","1","1","25",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air2_Alarm ,"]
["202","6.8.96.2","Air2_CloggedFilterAlarm","Clogged Filter","4","2","1","1","27",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air2_Alarm ,"]
["203","6.8.96.2","Air2_LossofAirFlowAlarm","Loss of Air2 Flow","4","2","1","1","29",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["204","6.8.96.2","Air2_HeaterOverheatingAlarm","Heater Overheating","4","2","1","1","30",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air2_Alarm ,"]
["205","6.8.96.2","Air2_Circuit1HighPressureAlarm","Circuit 1 High Pressure","4","2","1","1","31",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air2_Alarm ,"]
["206","6.8.96.2","Air2_Circuit2HighPressureAlarm","Circuit 2 High Pressure","4","2","1","1","32",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air2_Alarm ,"]
["207","6.8.96.2","Air2_Circuit1LowPressureAlarm","Circuit 1 Low Pressure","4","2","1","1","33",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air2_Alarm ,"]
["208","6.8.96.2","Air2_Circuit2LowPressureAlarm","Circuit 2 Low Pressure","4","2","1","1","34",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air2_Alarm ,"]
["209","6.8.96.2","Air2_Humidifier_WaterLossAlarm","Humidifier: Water Loss","4","2","1","1","42",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air2_Alarm ,"]
["210","6.8.96.2","Air2_HumidifierGeneral Alarm","Humidifier General","4","2","1","1","66",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air2_Alarm ,"]
["211","6.8.96.2","Air2_UnitOnAlarm","Unit on","4","2","1","1","67",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air2_Alarm ,"]
["212","6.8.96.2","Air2_UnitON/OFFSwitch","Unit ON/OFF Switch","4","2","1","1","76",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","Air conditioning2 Unit1 Switch OFF ,"]
["213","6.8.96.2","Air2_RoomTemperature","Room Temperature","4","2","1","3","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["214","6.8.96.2","Air2_OutdoorTemperature","Outdoor Temperature","4","2","1","3","3",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["215","6.8.96.2","Air2_RoomRelativeHumidity","Room Relative Humidity","4","2","1","3","7",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["216","6.8.96.2","Air2_OutletChilledWaterTemperature","Outlet Chilled Water Temperature","4","2","1","3","8",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["217","6.8.96.3","Air3_SystemOn","System On","4","2","1","1","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["218","6.8.96.3","Air3_Compressor_1","Compressor 1","4","2","1","1","3",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["219","6.8.96.3","Air3_Compressor_2","Compressor 2","4","2","1","1","4",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["220","6.8.96.3","Air3_Compressor_3","Compressor 3","4","2","1","1","5",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["221","6.8.96.3","Air3_Compressor_4","Compressor 4","4","2","1","1","6",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["222","6.8.96.3","Air3_El_Heater1","El. Heater 1","4","2","1","1","7",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["223","6.8.96.3","Air3_El_Heater2","El. Heater 2","4","2","1","1","8",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["224","6.8.96.3","Air3_Dehumidification","Dehumidification","4","2","1","1","11",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["225","6.8.96.3","Air3_Humidification","Humidification","4","2","1","1","12",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["226","6.8.96.3","Air3_HighRoomTemperatureAlarm","High Room Temperature","4","2","1","1","22",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air3_Alarm ,"]
["227","6.8.96.3","Air3_LowRoomTemperatureAlarm","Low Room Temperature","4","2","1","1","23",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air3_Alarm ,"]
["228","6.8.96.3","Air3_HighRoomHumidityAlarm","High Room Humidity","4","2","1","1","24",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air3_Alarm ,"]
["229","6.8.96.3","Air3_LowRoomHumidityAlarm","Low Room Humidity","4","2","1","1","25",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air3_Alarm ,"]
["230","6.8.96.3","Air3_CloggedFilterAlarm","Clogged Filter","4","2","1","1","27",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air3_Alarm ,"]
["231","6.8.96.3","Air3_LossofAir3FlowAlarm","Loss of Air3 Flow","4","2","1","1","29",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["232","6.8.96.3","Air3_HeaterOverheatingAlarm","Heater Overheating","4","2","1","1","30",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air3_Alarm ,"]
["233","6.8.96.3","Air3_Circuit1HighPressureAlarm","Circuit 1 High Pressure","4","2","1","1","31",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air3_Alarm ,"]
["234","6.8.96.3","Air3_Circuit2HighPressureAlarm","Circuit 2 High Pressure","4","2","1","1","32",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air3_Alarm ,"]
["235","6.8.96.3","Air3_Circuit1LowPressureAlarm","Circuit 1 Low Pressure","4","2","1","1","33",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air3_Alarm ,"]
["236","6.8.96.3","Air3_Circuit2LowPressureAlarm","Circuit 2 Low Pressure","4","2","1","1","34",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air3_Alarm ,"]
["237","6.8.96.3","Air3_Humidifier_WaterLossAlarm","Humidifier: Water Loss","4","2","1","1","42",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air3_Alarm ,"]
["238","6.8.96.3","Air3_HumidifierGeneral Alarm","Humidifier General","4","2","1","1","66",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air3_Alarm ,"]
["239","6.8.96.3","Air3_UnitOnAlarm","Unit on","4","2","1","1","67",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air3_Alarm ,"]
["240","6.8.96.3","Air3_UnitON/OFFSwitch","Unit ON/OFF Switch","4","2","1","1","76",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","Air conditioning3 Unit1 Switch OFF ,"]
["241","6.8.96.3","Air3_RoomTemperature","Room Temperature","4","2","1","3","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["242","6.8.96.3","Air3_OutdoorTemperature","Outdoor Temperature","4","2","1","3","3",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["243","6.8.96.3","Air3_RoomRelativeHumidity","Room Relative Humidity","4","2","1","3","7",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["244","6.8.96.3","Air3_OutletChilledWaterTemperature","Outlet Chilled Water Temperature","4","2","1","3","8",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["245","6.8.96.4","Air4_SystemOn","System On","4","2","1","1","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["246","6.8.96.4","Air4_Compressor_1","Compressor 1","4","2","1","1","3",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["247","6.8.96.4","Air4_Compressor_2","Compressor 2","4","2","1","1","4",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["248","6.8.96.4","Air4_Compressor_3","Compressor 3","4","2","1","1","5",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["249","6.8.96.4","Air4_Compressor_4","Compressor 4","4","2","1","1","6",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["250","6.8.96.4","Air4_El_Heater1","El. Heater 1","4","2","1","1","7",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["251","6.8.96.4","Air4_El_Heater2","El. Heater 2","4","2","1","1","8",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["252","6.8.96.4","Air4_Dehumidification","Dehumidification","4","2","1","1","11",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["253","6.8.96.4","Air4_Humidification","Humidification","4","2","1","1","12",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["254","6.8.96.4","Air4_HighRoomTemperatureAlarm","High Room Temperature","4","2","1","1","22",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air4_Alarm ,"]
["255","6.8.96.4","Air4_LowRoomTemperatureAlarm","Low Room Temperature","4","2","1","1","23",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air4_Alarm ,"]
["256","6.8.96.4","Air4_HighRoomHumidityAlarm","High Room Humidity","4","2","1","1","24",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air4_Alarm ,"]
["257","6.8.96.4","Air4_LowRoomHumidityAlarm","Low Room Humidity","4","2","1","1","25",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air4_Alarm ,"]
["258","6.8.96.4","Air4_CloggedFilterAlarm","Clogged Filter","4","2","1","1","27",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air4_Alarm ,"]
["259","6.8.96.4","Air4_LossofAir4FlowAlarm","Loss of Air4 Flow","4","2","1","1","29",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["260","6.8.96.4","Air4_HeaterOverheatingAlarm","Heater Overheating","4","2","1","1","30",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air4_Alarm ,"]
["261","6.8.96.4","Air4_Circuit1HighPressureAlarm","Circuit 1 High Pressure","4","2","1","1","31",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air4_Alarm ,"]
["262","6.8.96.4","Air4_Circuit2HighPressureAlarm","Circuit 2 High Pressure","4","2","1","1","32",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air4_Alarm ,"]
["263","6.8.96.4","Air4_Circuit1LowPressureAlarm","Circuit 1 Low Pressure","4","2","1","1","33",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air4_Alarm ,"]
["264","6.8.96.4","Air4_Circuit2LowPressureAlarm","Circuit 2 Low Pressure","4","2","1","1","34",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air4_Alarm ,"]
["265","6.8.96.4","Air4_Humidifier_WaterLossAlarm","Humidifier: Water Loss","4","2","1","1","42",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air4_Alarm ,"]
["266","6.8.96.4","Air4_HumidifierGeneral Alarm","Humidifier General","4","2","1","1","66",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air4_Alarm ,"]
["267","6.8.96.4","Air4_UnitOnAlarm","Unit on","4","2","1","1","67",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air4_Alarm ,"]
["268","6.8.96.4","Air4_UnitON/OFFSwitch","Unit ON/OFF Switch","4","2","1","1","76",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","Air conditioning4 Unit1 Switch OFF ,"]
["269","6.8.96.4","Air4_RoomTemperature","Room Temperature","4","2","1","3","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["270","6.8.96.4","Air4_OutdoorTemperature","Outdoor Temperature","4","2","1","3","3",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["271","6.8.96.4","Air4_RoomRelativeHumidity","Room Relative Humidity","4","2","1","3","7",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["272","6.8.96.4","Air4_OutletChilledWaterTemperature","Outlet Chilled Water Temperature","4","2","1","3","8",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["273","0.0.0.0","SystemCommunction","服务器通信状态","1001","0","0","0","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"900","1.0000000000","3","0","1","1","0","0","0","0","0",{"$nulls":3},"0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["273","6.8.96.1","Air1_UnitON/OFF","Unit ON/OFF","4","2","1","1","76",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","1","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["274","6.8.96.2","Air2_UnitON/OFF","Unit ON/OFF","4","2","1","1","76",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","1","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["275","6.8.96.3","Air3_UnitON/OFF","Unit ON/OF","4","2","1","1","76",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","1","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["276","6.8.96.4","Air4_UnitON/OFF","Unit ON/OFF","4","2","1","1","76",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","1","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["1","9.1.114.1","TEPW1_A_Phase","A_PhaseVoltageElectricityMeter","4","2","1","3","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","9.1.114.1","TEPW1_B_Phase","B_PhaseVoltageElectricityMeter","4","2","1","3","16",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","9.1.114.1","TEPW1_C_Phase","B_PhaseVoltageElectricityMeter","4","2","1","3","32",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","9.1.114.1","TEPW1_Aver_Phase","Electricity meter phase voltage","4","2","1","3","50",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","9.1.114.1","TEPW1_A_Curr","A three-phase power meter","4","2","1","3","4",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","A","900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","9.1.114.1","TEPW1_B_Curr","B three-phase power meter","4","2","1","3","20",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","A","900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","9.1.114.1","TEPW1_C_Curr","C three-phase power meter","4","2","1","3","36",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","A","900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","9.1.114.1","TEPW1_Aver_Curr","Electricity meter and current","4","2","1","3","52",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","A","900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","9.1.114.1","TEPW1_Freq","Electricity meter frequency","3","2","1","3","54",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","900","0.0010681300","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","9.1.114.1","TEPW1_AHavePower","Electricity meter A phase power dispatch","4","2","1","3","8",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","kw","900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","9.1.114.1","TEPW1_BHavePower","Electricity meter B phase power dispatch","4","2","1","3","24",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","kw","900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","9.1.114.1","TEPW1_CHavePower","Electricity meter C phase power dispatch","4","2","1","3","40",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","kw","900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","9.1.114.1","TEPW1_Aver_HavePower","Electricity meter in conjunction with the active power","4","2","1","3","56",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","kw","900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","9.1.114.1","TEPW1_A_Line","A line voltage electricity meter","4","2","1","3","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["15","9.1.114.1","TEPW1_B_Line","B line voltage electricity meter","4","2","1","3","18",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","9.1.114.1","TEPW1_C_Line","C line voltage electricity meter","4","2","1","3","34",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","9.1.114.2","TEPW2_A_Phase","A_PhaseVoltageElectricityMeter","4","2","1","3","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["18","9.1.114.2","TEPW2_B_Phase","B_PhaseVoltageElectricityMeter","4","2","1","3","16",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["19","9.1.114.2","TEPW2_C_Phase","B_PhaseVoltageElectricityMeter","4","2","1","3","32",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["20","9.1.114.2","TEPW2_Aver_Phase","Electricity meter phase voltage","4","2","1","3","50",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["21","9.1.114.2","TEPW2_A_Curr","A three-phase power meter","4","2","1","3","4",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","A","900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","9.1.114.2","TEPW2_B_Curr","B three-phase power meter","4","2","1","3","20",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","A","900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","9.1.114.2","TEPW2_C_Curr","C three-phase power meter","4","2","1","3","36",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","A","900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["24","9.1.114.2","TEPW2_Aver_Curr","Electricity meter and current","4","2","1","3","52",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","A","900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["25","9.1.114.2","TEPW2_Freq","Electricity meter frequency","3","2","1","3","54",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","900","0.0010681300","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["26","9.1.114.2","TEPW2_AHavePower","Electricity meter A phase power dispatch","4","2","1","3","8",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","kw","900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["27","9.1.114.2","TEPW2_BHavePower","Electricity meter B phase power dispatch","4","2","1","3","24",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","kw","900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["28","9.1.114.2","TEPW2_CHavePower","Electricity meter C phase power dispatch","4","2","1","3","40",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","kw","900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["29","9.1.114.2","TEPW2_Aver_HavePower","Electricity meter in conjunction with the active power","4","2","1","3","56",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","kw","900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["30","9.1.114.2","TEPW2_A_Line","A line voltage electricity meter","4","2","1","3","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["31","9.1.114.2","TEPW2_B_Line","B line voltage electricity meter","4","2","1","3","18",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["32","9.1.114.2","TEPW2_C_Line","C line voltage electricity meter","4","2","1","3","34",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["33","9.1.114.3","TEPW3_A_Phase","A_PhaseVoltageElectricityMeter","4","2","1","3","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["34","9.1.114.3","TEPW3_B_Phase","B_PhaseVoltageElectricityMeter","4","2","1","3","16",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["35","9.1.114.3","TEPW3_C_Phase","B_PhaseVoltageElectricityMeter","4","2","1","3","32",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["36","9.1.114.3","TEPW3_Aver_Phase","Electricity meter phase voltage","4","2","1","3","50",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["37","9.1.114.3","TEPW3_A_Curr","A three-phase power meter","4","2","1","3","4",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","A","900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["38","9.1.114.3","TEPW3_B_Curr","B three-phase power meter","4","2","1","3","20",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","A","900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["39","9.1.114.3","TEPW3_C_Curr","C three-phase power meter","4","2","1","3","36",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","A","900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["40","9.1.114.3","TEPW3_Aver_Curr","Electricity meter and current","4","2","1","3","52",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","A","900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["41","9.1.114.3","TEPW3_Freq","Electricity meter frequency","3","2","1","3","54",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","900","0.0010681300","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["42","9.1.114.3","TEPW3_AHavePower","Electricity meter A phase power dispatch","4","2","1","3","8",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","kw","900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["43","9.1.114.3","TEPW3_BHavePower","Electricity meter B phase power dispatch","4","2","1","3","24",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","kw","900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["44","9.1.114.3","TEPW3_CHavePower","Electricity meter C phase power dispatch","4","2","1","3","40",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","kw","900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["45","9.1.114.3","TEPW3_Aver_HavePower","Electricity meter in conjunction with the active power","4","2","1","3","56",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","kw","900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["46","9.1.114.3","TEPW3_A_Line","A line voltage electricity meter","4","2","1","3","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["47","9.1.114.3","TEPW3_B_Line","B line voltage electricity meter","4","2","1","3","18",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["48","9.1.114.3","TEPW3_C_Line","C line voltage electricity meter","4","2","1","3","34",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["49","9.1.114.4","TEPW4_A_Phase","A_PhaseVoltageElectricityMeter","4","2","1","3","0",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["50","9.1.114.4","TEPW4_B_Phase","B_PhaseVoltageElectricityMeter","4","2","1","3","16",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["51","9.1.114.4","TEPW4_C_Phase","B_PhaseVoltageElectricityMeter","4","2","1","3","32",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["52","9.1.114.4","TEPW4_Aver_Phase","Electricity meter phase voltage","4","2","1","3","50",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["53","9.1.114.4","TEPW4_A_Curr","A three-phase power meter","4","2","1","3","4",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","A","900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["54","9.1.114.4","TEPW4_B_Curr","B three-phase power meter","4","2","1","3","20",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","A","900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["55","9.1.114.4","TEPW4_C_Curr","C three-phase power meter","4","2","1","3","36",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","A","900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["56","9.1.114.4","TEPW4_Aver_Curr","Electricity meter and current","4","2","1","3","52",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","A","900","0.0001000000","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["57","9.1.114.4","TEPW4_Freq","Electricity meter frequency","3","2","1","3","54",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","900","0.0010681300","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["58","9.1.114.4","TEPW4_AHavePower","Electricity meter A phase power dispatch","4","2","1","3","8",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","kw","900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["59","9.1.114.4","TEPW4_BHavePower","Electricity meter B phase power dispatch","4","2","1","3","24",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","kw","900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["60","9.1.114.4","TEPW4_CHavePower","Electricity meter C phase power dispatch","4","2","1","3","40",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","kw","900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["61","9.1.114.4","TEPW4_Aver_HavePower","Electricity meter in conjunction with the active power","4","2","1","3","56",null,null,"0","30","60","1",null,null,"5","0","300","0","0","0","0","0","0","kw","900","0.4000000060","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["62","9.1.114.4","TEPW4_A_Line","A line voltage electricity meter","4","2","1","3","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["63","9.1.114.4","TEPW4_B_Line","B line voltage electricity meter","4","2","1","3","18",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["64","9.1.114.4","TEPW4_C_Line","C line voltage electricity meter","4","2","1","3","34",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","V","900","0.0099999998","3","0","1","1","0","0","0","0","114",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["65","5.29.128.1","AKCP_1_Temp","Port 1 temperature","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.16.1.3.0","public","0","0","0","0","15","32","0","0","0","癈","300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0","0","0"]
["66","5.29.128.1","AKCP_1_Humidity","Port 1 humidity","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.17.1.3.0","public","0","0","0","0","20","85","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0","0","0"]
["67","5.29.128.1","AKCP_2_Temp","Port 2 temperature","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.16.1.3.1","public","0","0","0","0","15","32","0","0","0","癈","300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0","0","0"]
["68","5.29.128.1","AKCP_2_Humidity","Port 2 humidity","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.17.1.3.1","public","0","0","0","0","20","85","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0","0","0"]
["69","5.29.128.1","AKCP_3_Temp","Port 3 temperature","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.16.1.3.2","public","0","0","0","0","15","32","0","0","0","癈","300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0","0","0"]
["70","5.29.128.1","AKCP_3_Humidity","Port 3 humidity","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.17.1.3.2","public","0","0","0","0","20","85","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0","0","0"]
["71","5.29.128.1","AKCP_4_Temp","Port 4 temperature","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.16.1.3.3","public","0","0","0","0","15","32","0","0","0","癈","300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0","0","0"]
["72","5.29.128.1","AKCP_4_Humidity","Port 4 humidity","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.17.1.3.3","public","0","0","0","0","20","85","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0","0","0"]
["73","5.29.128.1","AKCP_5_Temp","Port 5 temperature","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.16.1.3.4","public","0","0","0","0","15","32","0","0","0","癈","300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0","0","0"]
["74","5.29.128.1","AKCP_5_Humidity","Port 5 humidity","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.17.1.3.4","public","0","0","0","0","20","85","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0","0","0"]
["75","5.29.128.1","AKCP_6_Temp","Port 6 temperature","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.16.1.3.5","public","0","0","0","0","15","32","0","0","0","癈","300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0","0","0"]
["76","5.29.128.1","AKCP_6_Humidity","Port 6 humidity","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.17.1.3.5","public","0","0","0","0","20","85","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0","0","0"]
["77","5.29.128.1","AKCP_7_Temp","Port 7 temperature","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.16.1.3.6","public","0","0","0","0","15","32","0","0","0","癈","300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0","0","0"]
["78","5.29.128.1","AKCP_7_Humidity","Port 7 humidity","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.17.1.3.6","public","0","0","0","0","20","85","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0","0","0"]
["79","5.29.128.1","AKCP_8_Temp","Port 8 temperature","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.16.1.3.7","public","0","0","0","0","15","32","0","0","0","癈","300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0","0","0"]
["80","5.29.128.1","AKCP_8_Humidity","Port 8 humidity","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.17.1.3.7","public","0","0","0","0","20","85","0","0","0","%","300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","0","0","0"]
["81","7.33.132.1","FG_ALS_1_Line_Leak","leaking","4","2","1","3","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","m","300","1.0000000000","3","0","1","1","0","0","0","0","132",null,null,"0","0","0","FG_ALS_1_Line_LeakPos",{"$nulls":9},"0","0","0","0","0","0","0","0","0","0","1","1","0","0","0","0","0","0","0","0","1","1,","alarm,"]
["82","7.33.132.1","FG_ALS_1_Line_CableCut","break","4","2","1","3","4",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","132",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["83","7.33.132.1","FG_ALS_1_Line_LeakPos","Leaking location","4","2","1","3","6",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0","m","300","1.0000000000","3","0","1","1","0","0","0","0","132",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["84","5.29.128.1","AKCP_Smoke","Port 9 Smoke","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.18.1.3.8","public","0","0","0","0","0","0","2","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","6,","Smoke Alarm,"]
["85","5.29.128.1","AKCP_Oil_Machine","Port 10 Oil_Machine","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.18.1.3.9","public","0","0","0","0","0","0","2","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","6,","OilMachine Alarm,"]
["86","5.29.128.1","AKCP_Security","Port 11 Security","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.3854.1.2.2.1.18.1.3.10","public","0","0","0","0","0","0","2","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","128",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","6,","Security Alarm,"]
["87","4.11.18.1","UPS1_systemStatus","UPS1systemStatus","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.1.1.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","2","0,",","]
["88","4.11.18.1","UPS1_inletAirTemperature","inletAirTemperature","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.1.2.0","public","0","0","0","0","15","32","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["89","4.11.18.1","UPS1_dcBusVoltage","dcBusVoltage","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.1.3.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["90","4.11.18.1","UPS1_inputLineVoltageA","inputLineVoltageA","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.1.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["91","4.11.18.1","UPS1_inputLineVoltageB","inputLineVoltageB","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.2.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["92","4.11.18.1","UPS1_inputLineVoltageC","inputLineVoltageC","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.3.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["93","4.11.18.1","UPS1_inputPhaseVoltageA","inputPhaseVoltageA","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.4.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["94","4.11.18.1","UPS1_inputPhaseVoltageB","inputPhaseVoltageB","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.5.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["95","4.11.18.1","UPS1_inputPhaseVoltageC","inputPhaseVoltageC","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.6.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["96","4.11.18.1","UPS1_inputCurrentA","inputCurrentA","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.7.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["97","4.11.18.1","UPS1_inputCurrentB","inputCurrentB","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.8.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["98","4.11.18.1","UPS1_inputCurrentC","inputCurrentC","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.9.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["99","4.11.18.1","UPS1_inputFrequency","inputFrequency","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.10.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["100","4.11.18.1","UPS1_bypassPhaseVoltageA","bypassPhaseVoltageA","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.3.1.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["101","4.11.18.1","UPS1_bypassPhaseVoltageB","bypassPhaseVoltageB","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.3.2.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["102","4.11.18.1","UPS1_bypassPhaseVoltageC","bypassPhaseVoltageC","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.3.3.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["103","4.11.18.1","UPS1_bypassFrequency","bypassFrequency","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.3.4.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["104","4.11.18.1","UPS1_outputPhaseVoltageA","outputPhaseVoltageA","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.1.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["105","4.11.18.1","UPS1_outputPhaseVoltageB","outputPhaseVoltageB","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.2.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["106","4.11.18.1","UPS1_outputPhaseVoltageC","outputPhaseVoltageC","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.3.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["107","4.11.18.1","UPS1_outputCurrentA","outputCurrentA","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.4.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["108","4.11.18.1","UPS1_outputCurrentB","outputCurrentB","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.5.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["109","4.11.18.1","UPS1_outputCurrentC","outputCurrentC","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.6.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["110","4.11.18.1","UPS1_outputFrequency","outputFrequency","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.7.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["111","4.11.18.1","UPS1_outputActivePowerA","outputActivePowerA","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.11.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["112","4.11.18.1","UPS1_outputActivePowerB","outputActivePowerB","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.12.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["113","4.11.18.1","UPS1_outputActivePowerC","outputActivePowerC","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.13.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["114","4.11.18.1","UPS1_outputApparentPowerA","outputApparentPowerA","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.14.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["115","4.11.18.1","UPS1_outputApparentPowerB","outputApparentPowerB","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.15.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["116","4.11.18.1","UPS1_outputApparentPowerC","outputApparentPowerC","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.16.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["117","4.11.18.1","UPS1_outputLoadA","outputLoadA","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.20.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["118","4.11.18.1","UPS1_outputLoadB","outputLoadB","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.21.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["119","4.11.18.1","UPS1_outputLoadC","outputLoadC","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.22.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["120","4.11.18.1","UPS1_batteryVoltage","batteryVoltage","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.5.1.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["121","4.11.18.1","UPS1_batteryCurrent","batteryCurrent","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.5.2.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["122","4.11.18.1","UPS1_batteryRemainsTime","batteryRemainsTime","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.5.3.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["123","4.11.18.1","UPS1_batteryTemperature","batteryTemperature","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.5.4.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["124","4.11.18.2","UPS2_systemStatus","UPS2systemStatus","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.1.1.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","2","0,",","]
["125","4.11.18.2","UPS2_inletAirTemperature","inletAirTemperature","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.1.2.0","public","0","0","0","0","15","32","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["126","4.11.18.2","UPS2_dcBusVoltage","dcBusVoltage","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.1.3.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["127","4.11.18.2","UPS2_inputLineVoltageA","inputLineVoltageA","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.1.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["128","4.11.18.2","UPS2_inputLineVoltageB","inputLineVoltageB","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.2.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["129","4.11.18.2","UPS2_inputLineVoltageC","inputLineVoltageC","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.3.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["130","4.11.18.2","UPS2_inputPhaseVoltageA","inputPhaseVoltageA","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.4.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["131","4.11.18.2","UPS2_inputPhaseVoltageB","inputPhaseVoltageB","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.5.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["132","4.11.18.2","UPS2_inputPhaseVoltageC","inputPhaseVoltageC","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.6.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["133","4.11.18.2","UPS2_inputCurrentA","inputCurrentA","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.7.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["134","4.11.18.2","UPS2_inputCurrentB","inputCurrentB","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.8.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["135","4.11.18.2","UPS2_inputCurrentC","inputCurrentC","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.9.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["136","4.11.18.2","UPS2_inputFrequency","inputFrequency","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.2.10.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["137","4.11.18.2","UPS2_bypassPhaseVoltageA","bypassPhaseVoltageA","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.3.1.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["138","4.11.18.2","UPS2_bypassPhaseVoltageB","bypassPhaseVoltageB","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.3.2.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["139","4.11.18.2","UPS2_bypassPhaseVoltageC","bypassPhaseVoltageC","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.3.3.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["140","4.11.18.2","UPS2_bypassFrequency","bypassFrequency","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.3.4.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["141","4.11.18.2","UPS2_outputPhaseVoltageA","outputPhaseVoltageA","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.1.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["142","4.11.18.2","UPS2_outputPhaseVoltageB","outputPhaseVoltageB","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.2.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["143","4.11.18.2","UPS2_outputPhaseVoltageC","outputPhaseVoltageC","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.3.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["144","4.11.18.2","UPS2_outputCurrentA","outputCurrentA","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.4.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["145","4.11.18.2","UPS2_outputCurrentB","outputCurrentB","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.5.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["146","4.11.18.2","UPS2_outputCurrentC","outputCurrentC","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.6.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["147","4.11.18.2","UPS2_outputFrequency","outputFrequency","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.7.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["148","4.11.18.2","UPS2_outputActivePowerA","outputActivePowerA","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.11.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["149","4.11.18.2","UPS2_outputActivePowerB","outputActivePowerB","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.12.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["150","4.11.18.2","UPS2_outputActivePowerC","outputActivePowerC","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.13.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["151","4.11.18.2","UPS2_outputApparentPowerA","outputApparentPowerA","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.14.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["152","4.11.18.2","UPS2_outputApparentPowerB","outputApparentPowerB","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.15.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["153","4.11.18.2","UPS2_outputApparentPowerC","outputApparentPowerC","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.16.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["154","4.11.18.2","UPS2_outputLoadA","outputLoadA","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.20.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["155","4.11.18.2","UPS2_outputLoadB","outputLoadB","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.21.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["156","4.11.18.2","UPS2_outputLoadC","outputLoadC","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.4.22.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["157","4.11.18.2","UPS2_batteryVoltage","batteryVoltage","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.5.1.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["158","4.11.18.2","UPS2_batteryCurrent","batteryCurrent","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.5.2.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["159","4.11.18.2","UPS2_batteryRemainsTime","batteryRemainsTime","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.5.3.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["160","4.11.18.2","UPS2_batteryTemperature","batteryTemperature","1","0","0","1","0",null,null,"0","30","60","1","1.3.6.1.4.1.13400.2.14.2.5.4.0","public","0","0","0","0","0","0","0","0","0",null,"300","0.0099999998","0","0","1","1","0","0","0","0","18",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["161","6.8.96.1","Air1_SystemOn","System On","4","2","1","1","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["162","6.8.96.1","Air1_Compressor_1","Compressor 1","4","2","1","1","3",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["163","6.8.96.1","Air1_Compressor_2","Compressor 2","4","2","1","1","4",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["164","6.8.96.1","Air1_Compressor_3","Compressor 3","4","2","1","1","5",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["165","6.8.96.1","Air1_Compressor_4","Compressor 4","4","2","1","1","6",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["166","6.8.96.1","Air1_El_Heater1","El. Heater 1","4","2","1","1","7",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["167","6.8.96.1","Air1_El_Heater2","El. Heater 2","4","2","1","1","8",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["168","6.8.96.1","Air1_Dehumidification","Dehumidification","4","2","1","1","11",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["169","6.8.96.1","Air1_Humidification","Humidification","4","2","1","1","12",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["170","6.8.96.1","Air1_HighRoomTemperatureAlarm","High Room Temperature","4","2","1","1","22",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air1_Alarm ,"]
["171","6.8.96.1","Air1_LowRoomTemperatureAlarm","Low Room Temperature","4","2","1","1","23",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air1_Alarm ,"]
["172","6.8.96.1","Air1_HighRoomHumidityAlarm","High Room Humidity","4","2","1","1","24",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air1_Alarm ,"]
["173","6.8.96.1","Air1_LowRoomHumidityAlarm","Low Room Humidity","4","2","1","1","25",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air1_Alarm ,"]
["174","6.8.96.1","Air1_CloggedFilterAlarm","Clogged Filter","4","2","1","1","27",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air1_Alarm ,"]
["175","6.8.96.1","Air1_LossofAirFlowAlarm","Loss of Air1 Flow","4","2","1","1","29",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["176","6.8.96.1","Air1_HeaterOverheatingAlarm","Heater Overheating","4","2","1","1","30",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air1_Alarm ,"]
["177","6.8.96.1","Air1_Circuit1HighPressureAlarm","Circuit 1 High Pressure","4","2","1","1","31",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air1_Alarm ,"]
["178","6.8.96.1","Air1_Circuit2HighPressureAlarm","Circuit 2 High Pressure","4","2","1","1","32",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air1_Alarm ,"]
["179","6.8.96.1","Air1_Circuit1LowPressureAlarm","Circuit 1 Low Pressure","4","2","1","1","33",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air1_Alarm ,"]
["180","6.8.96.1","Air1_Circuit2LowPressureAlarm","Circuit 2 Low Pressure","4","2","1","1","34",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air1_Alarm ,"]
["181","6.8.96.1","Air1_Humidifier_WaterLossAlarm","Humidifier: Water Loss","4","2","1","1","42",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air1_Alarm ,"]
["182","6.8.96.1","Air1_HumidifierGeneral Alarm","Humidifier General","4","2","1","1","66",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air1_Alarm ,"]
["183","6.8.96.1","Air1_UnitOnAlarm","Unit on","4","2","1","1","67",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air1_Alarm ,"]
["184","6.8.96.1","Air1_UnitON/OFFSwitch","Unit ON/OFF Switch","4","2","1","1","76",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air conditioning1 Unit1 Switch OFF ,"]
["185","6.8.96.1","Air1_RoomTemperature","Room Temperature","4","2","1","3","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["186","6.8.96.1","Air1_OutdoorTemperature","Outdoor Temperature","4","2","1","3","3",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["187","6.8.96.1","Air1_RoomRelativeHumidity","Room Relative Humidity","4","2","1","3","7",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["188","6.8.96.1","Air1_OutletChilledWaterTemperature","Outlet Chilled Water Temperature","4","2","1","3","8",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["189","6.8.96.2","Air2_SystemOn","System On","4","2","1","1","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["190","6.8.96.2","Air2_Compressor_1","Compressor 1","4","2","1","1","3",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["191","6.8.96.2","Air2_Compressor_2","Compressor 2","4","2","1","1","4",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["192","6.8.96.2","Air2_Compressor_3","Compressor 3","4","2","1","1","5",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["193","6.8.96.2","Air2_Compressor_4","Compressor 4","4","2","1","1","6",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["194","6.8.96.2","Air2_El_Heater1","El. Heater 1","4","2","1","1","7",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["195","6.8.96.2","Air2_El_Heater2","El. Heater 2","4","2","1","1","8",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["196","6.8.96.2","Air2_Dehumidification","Dehumidification","4","2","1","1","11",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["197","6.8.96.2","Air2_Humidification","Humidification","4","2","1","1","12",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["198","6.8.96.2","Air2_HighRoomTemperatureAlarm","High Room Temperature","4","2","1","1","22",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air2_Alarm ,"]
["199","6.8.96.2","Air2_LowRoomTemperatureAlarm","Low Room Temperature","4","2","1","1","23",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air2_Alarm ,"]
["200","6.8.96.2","Air2_HighRoomHumidityAlarm","High Room Humidity","4","2","1","1","24",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air2_Alarm ,"]
["201","6.8.96.2","Air2_LowRoomHumidityAlarm","Low Room Humidity","4","2","1","1","25",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air2_Alarm ,"]
["202","6.8.96.2","Air2_CloggedFilterAlarm","Clogged Filter","4","2","1","1","27",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air2_Alarm ,"]
["203","6.8.96.2","Air2_LossofAirFlowAlarm","Loss of Air2 Flow","4","2","1","1","29",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["204","6.8.96.2","Air2_HeaterOverheatingAlarm","Heater Overheating","4","2","1","1","30",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air2_Alarm ,"]
["205","6.8.96.2","Air2_Circuit1HighPressureAlarm","Circuit 1 High Pressure","4","2","1","1","31",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air2_Alarm ,"]
["206","6.8.96.2","Air2_Circuit2HighPressureAlarm","Circuit 2 High Pressure","4","2","1","1","32",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air2_Alarm ,"]
["207","6.8.96.2","Air2_Circuit1LowPressureAlarm","Circuit 1 Low Pressure","4","2","1","1","33",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air2_Alarm ,"]
["208","6.8.96.2","Air2_Circuit2LowPressureAlarm","Circuit 2 Low Pressure","4","2","1","1","34",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air2_Alarm ,"]
["209","6.8.96.2","Air2_Humidifier_WaterLossAlarm","Humidifier: Water Loss","4","2","1","1","42",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air2_Alarm ,"]
["210","6.8.96.2","Air2_HumidifierGeneral Alarm","Humidifier General","4","2","1","1","66",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air2_Alarm ,"]
["211","6.8.96.2","Air2_UnitOnAlarm","Unit on","4","2","1","1","67",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air2_Alarm ,"]
["212","6.8.96.2","Air2_UnitON/OFFSwitch","Unit ON/OFF Switch","4","2","1","1","76",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","Air conditioning2 Unit1 Switch OFF ,"]
["213","6.8.96.2","Air2_RoomTemperature","Room Temperature","4","2","1","3","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["214","6.8.96.2","Air2_OutdoorTemperature","Outdoor Temperature","4","2","1","3","3",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["215","6.8.96.2","Air2_RoomRelativeHumidity","Room Relative Humidity","4","2","1","3","7",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["216","6.8.96.2","Air2_OutletChilledWaterTemperature","Outlet Chilled Water Temperature","4","2","1","3","8",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["217","6.8.96.3","Air3_SystemOn","System On","4","2","1","1","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["218","6.8.96.3","Air3_Compressor_1","Compressor 1","4","2","1","1","3",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["219","6.8.96.3","Air3_Compressor_2","Compressor 2","4","2","1","1","4",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["220","6.8.96.3","Air3_Compressor_3","Compressor 3","4","2","1","1","5",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["221","6.8.96.3","Air3_Compressor_4","Compressor 4","4","2","1","1","6",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["222","6.8.96.3","Air3_El_Heater1","El. Heater 1","4","2","1","1","7",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["223","6.8.96.3","Air3_El_Heater2","El. Heater 2","4","2","1","1","8",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["224","6.8.96.3","Air3_Dehumidification","Dehumidification","4","2","1","1","11",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["225","6.8.96.3","Air3_Humidification","Humidification","4","2","1","1","12",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["226","6.8.96.3","Air3_HighRoomTemperatureAlarm","High Room Temperature","4","2","1","1","22",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air3_Alarm ,"]
["227","6.8.96.3","Air3_LowRoomTemperatureAlarm","Low Room Temperature","4","2","1","1","23",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air3_Alarm ,"]
["228","6.8.96.3","Air3_HighRoomHumidityAlarm","High Room Humidity","4","2","1","1","24",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air3_Alarm ,"]
["229","6.8.96.3","Air3_LowRoomHumidityAlarm","Low Room Humidity","4","2","1","1","25",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air3_Alarm ,"]
["230","6.8.96.3","Air3_CloggedFilterAlarm","Clogged Filter","4","2","1","1","27",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air3_Alarm ,"]
["231","6.8.96.3","Air3_LossofAir3FlowAlarm","Loss of Air3 Flow","4","2","1","1","29",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["232","6.8.96.3","Air3_HeaterOverheatingAlarm","Heater Overheating","4","2","1","1","30",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air3_Alarm ,"]
["233","6.8.96.3","Air3_Circuit1HighPressureAlarm","Circuit 1 High Pressure","4","2","1","1","31",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air3_Alarm ,"]
["234","6.8.96.3","Air3_Circuit2HighPressureAlarm","Circuit 2 High Pressure","4","2","1","1","32",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air3_Alarm ,"]
["235","6.8.96.3","Air3_Circuit1LowPressureAlarm","Circuit 1 Low Pressure","4","2","1","1","33",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air3_Alarm ,"]
["236","6.8.96.3","Air3_Circuit2LowPressureAlarm","Circuit 2 Low Pressure","4","2","1","1","34",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air3_Alarm ,"]
["237","6.8.96.3","Air3_Humidifier_WaterLossAlarm","Humidifier: Water Loss","4","2","1","1","42",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air3_Alarm ,"]
["238","6.8.96.3","Air3_HumidifierGeneral Alarm","Humidifier General","4","2","1","1","66",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air3_Alarm ,"]
["239","6.8.96.3","Air3_UnitOnAlarm","Unit on","4","2","1","1","67",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air3_Alarm ,"]
["240","6.8.96.3","Air3_UnitON/OFFSwitch","Unit ON/OFF Switch","4","2","1","1","76",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","Air conditioning3 Unit1 Switch OFF ,"]
["241","6.8.96.3","Air3_RoomTemperature","Room Temperature","4","2","1","3","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["242","6.8.96.3","Air3_OutdoorTemperature","Outdoor Temperature","4","2","1","3","3",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["243","6.8.96.3","Air3_RoomRelativeHumidity","Room Relative Humidity","4","2","1","3","7",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["244","6.8.96.3","Air3_OutletChilledWaterTemperature","Outlet Chilled Water Temperature","4","2","1","3","8",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["245","6.8.96.4","Air4_SystemOn","System On","4","2","1","1","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["246","6.8.96.4","Air4_Compressor_1","Compressor 1","4","2","1","1","3",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["247","6.8.96.4","Air4_Compressor_2","Compressor 2","4","2","1","1","4",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["248","6.8.96.4","Air4_Compressor_3","Compressor 3","4","2","1","1","5",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["249","6.8.96.4","Air4_Compressor_4","Compressor 4","4","2","1","1","6",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["250","6.8.96.4","Air4_El_Heater1","El. Heater 1","4","2","1","1","7",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["251","6.8.96.4","Air4_El_Heater2","El. Heater 2","4","2","1","1","8",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["252","6.8.96.4","Air4_Dehumidification","Dehumidification","4","2","1","1","11",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["253","6.8.96.4","Air4_Humidification","Humidification","4","2","1","1","12",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["254","6.8.96.4","Air4_HighRoomTemperatureAlarm","High Room Temperature","4","2","1","1","22",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air4_Alarm ,"]
["255","6.8.96.4","Air4_LowRoomTemperatureAlarm","Low Room Temperature","4","2","1","1","23",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air4_Alarm ,"]
["256","6.8.96.4","Air4_HighRoomHumidityAlarm","High Room Humidity","4","2","1","1","24",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air4_Alarm ,"]
["257","6.8.96.4","Air4_LowRoomHumidityAlarm","Low Room Humidity","4","2","1","1","25",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air4_Alarm ,"]
["258","6.8.96.4","Air4_CloggedFilterAlarm","Clogged Filter","4","2","1","1","27",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air4_Alarm ,"]
["259","6.8.96.4","Air4_LossofAir4FlowAlarm","Loss of Air4 Flow","4","2","1","1","29",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Alarm,"]
["260","6.8.96.4","Air4_HeaterOverheatingAlarm","Heater Overheating","4","2","1","1","30",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air4_Alarm ,"]
["261","6.8.96.4","Air4_Circuit1HighPressureAlarm","Circuit 1 High Pressure","4","2","1","1","31",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air4_Alarm ,"]
["262","6.8.96.4","Air4_Circuit2HighPressureAlarm","Circuit 2 High Pressure","4","2","1","1","32",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air4_Alarm ,"]
["263","6.8.96.4","Air4_Circuit1LowPressureAlarm","Circuit 1 Low Pressure","4","2","1","1","33",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air4_Alarm ,"]
["264","6.8.96.4","Air4_Circuit2LowPressureAlarm","Circuit 2 Low Pressure","4","2","1","1","34",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air4_Alarm ,"]
["265","6.8.96.4","Air4_Humidifier_WaterLossAlarm","Humidifier: Water Loss","4","2","1","1","42",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air4_Alarm ,"]
["266","6.8.96.4","Air4_HumidifierGeneral Alarm","Humidifier General","4","2","1","1","66",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air4_Alarm ,"]
["267","6.8.96.4","Air4_UnitOnAlarm","Unit on","4","2","1","1","67",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","Air4_Alarm ,"]
["268","6.8.96.4","Air4_UnitON/OFFSwitch","Unit ON/OFF Switch","4","2","1","1","76",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","1","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","1","1,","Air conditioning4 Unit1 Switch OFF ,"]
["269","6.8.96.4","Air4_RoomTemperature","Room Temperature","4","2","1","3","2",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["270","6.8.96.4","Air4_OutdoorTemperature","Outdoor Temperature","4","2","1","3","3",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["271","6.8.96.4","Air4_RoomRelativeHumidity","Room Relative Humidity","4","2","1","3","7",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["272","6.8.96.4","Air4_OutletChilledWaterTemperature","Outlet Chilled Water Temperature","4","2","1","3","8",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","0","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","0","0","0"]
["273","6.8.96.1","Air1_UnitON/OFF","Unit ON/OFF","4","2","1","1","76",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","1","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["274","6.8.96.2","Air2_UnitON/OFF","Unit ON/OFF","4","2","1","1","76",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","1","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["275","6.8.96.3","Air3_UnitON/OFF","Unit ON/OF","4","2","1","1","76",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","1","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["276","6.8.96.4","Air4_UnitON/OFF","Unit ON/OFF","4","2","1","1","76",null,null,"0","30","60","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","0","1","1","1","0","0","0","0","96",null,null,"0","0","0",{"$nulls":10},"0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]