{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["变量dat文件"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"变量dat文件","index":0,"n_rows":99,"n_cols":76,"rows_kept":99,"flags":["formulas_cached_only"]}
["变量ID","设备Uid","变量名称","变量描述","变量类型ID","变量数据长度","请求寄存器个数","功能码id","寄存器起始地址","命令","类型","索引","辨识时间","重新检测等待时间","恢复正常是否触发远程报警","snmp对象oid","SNMP域","最大值","最小值","最大转换比率","最小转换比率","下限","上限","正常状态","校正值","偏移值","单位","采集频率","转换系数","告警级别","读写权限","是否保存数值","是否实时采集数据","是否记录实时曲线","是否允许DDE访问","寄存器子ID","位信息ID","设备类型ID","开的描述","关的描述","设定值","变量起始BIT位","变量终止BIT位","预留1_Str","预留2_Str","预留3_Str","预留4_Str","预留5_Str","预留6_Str","预留7_Str","预留8_Str","预留9_Str","预留10_Str","预留1_Int","预留2_Int","预留3_Int","预留4_Int","预留5_Int","预留6_Int","预留7_Int","预留8_Int","预留9_Int","预留10_Int","预留1_Bool","预留2_Bool","预留3_Bool","预留4_Bool","预留5_Bool","预留6_Bool","预留7_Bool","预留8_Bool","预留9_Bool","预留10_Bool","变量状态个数","变量状态ID","变量状态描述"]
["1","9.1.114.1","EM600_1_PhaseVoltageUa","1号电量仪A相电压","4","2","1","3","104",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["2","9.1.114.1","EM600_1_PhaseVoltageUb","1号电量仪B相电压","4","2","1","3","105",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["3","9.1.114.1","EM600_1_PhaseVoltageUc","1号电量仪C相电压","4","2","1","3","106",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["4","9.1.114.1","EM600_1_LineVoltageUca","1号电量仪A线电压","4","2","1","3","100",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["5","9.1.114.1","EM600_1_LineVoltageUab","1号电量仪B线电压","4","2","1","3","101",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["6","9.1.114.1","EM600_1_LineVoltageUbc","1号电量仪C线电压","4","2","1","3","102",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["7","9.1.114.1","EM600_1_PhaseCurrentIa","1号电量仪A相电流","4","2","1","3","108",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","21","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["8","9.1.114.1","EM600_1_PhaseCurrentIb","1号电量仪B相电流","4","2","1","3","109",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","21","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["9","9.1.114.1","EM600_1_PhaseCurrentIc","1号电量仪C相电流","4","2","1","3","110",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","21","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["10","9.1.114.1","EM600_1_PhaseActivePowerPa","1号电量仪A相有功功率","3","2","1","3","122",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","KW","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["11","9.1.114.1","EM600_1_PhaseActivePowerPb","1号电量仪B相有功功率","3","2","1","3","123",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","KW","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["12","9.1.114.1","EM600_1_PhaseActivePowerPc","1号电量仪C相有功功率","3","2","1","3","124",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","KW","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["13","9.1.114.1","EM600_1_Frequency","1号电量仪频率","4","2","1","3","113",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","66","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["14","9.1.114.1","EM600_1_Netstatus","1号电量仪通信","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
["15","9.1.114.2","EM600_2_PhaseVoltageUa","2号电量仪A相电压","4","2","1","3","104",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["16","9.1.114.2","EM600_2_PhaseVoltageUb","2号电量仪B相电压","4","2","1","3","105",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["17","9.1.114.2","EM600_2_PhaseVoltageUc","2号电量仪C相电压","4","2","1","3","106",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["18","9.1.114.2","EM600_2_LineVoltageUca","2号电量仪A线电压","4","2","1","3","100",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["19","9.1.114.2","EM600_2_LineVoltageUab","2号电量仪B线电压","4","2","1","3","101",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["20","9.1.114.2","EM600_2_LineVoltageUbc","2号电量仪C线电压","4","2","1","3","102",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["21","9.1.114.2","EM600_2_PhaseCurrentIa","2号电量仪A相电流","4","2","1","3","108",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","21","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["22","9.1.114.2","EM600_2_PhaseCurrentIb","2号电量仪B相电流","4","2","1","3","109",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","21","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["23","9.1.114.2","EM600_2_PhaseCurrentIc","2号电量仪C相电流","4","2","1","3","110",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","21","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["24","9.1.114.2","EM600_2_PhaseActivePowerPa","2号电量仪A相有功功率","3","2","1","3","122",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","KW","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["25","9.1.114.2","EM600_2_PhaseActivePowerPb","2号电量仪B相有功功率","3","2","1","3","123",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","KW","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["26","9.1.114.2","EM600_2_PhaseActivePowerPc","2号电量仪C相有功功率","3","2","1","3","124",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","KW","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["27","9.1.114.2","EM600_2_Frequency","2号电量仪频率","4","2","1","3","113",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","66","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["28","9.1.114.2","EM600_2_Netstatus","2号电量仪通信","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
["29","9.1.114.3","EM600_3_PhaseVoltageUa","3号电量仪A相电压","4","2","1","3","104",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["30","9.1.114.3","EM600_3_PhaseVoltageUb","3号电量仪B相电压","4","2","1","3","105",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["31","9.1.114.3","EM600_3_PhaseVoltageUc","3号电量仪C相电压","4","2","1","3","106",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["32","9.1.114.3","EM600_3_LineVoltageUca","3号电量仪A线电压","4","2","1","3","100",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["33","9.1.114.3","EM600_3_LineVoltageUab","3号电量仪B线电压","4","2","1","3","101",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["34","9.1.114.3","EM600_3_LineVoltageUbc","3号电量仪C线电压","4","2","1","3","102",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["35","9.1.114.3","EM600_3_PhaseCurrentIa","3号电量仪A相电流","4","2","1","3","108",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","21","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["36","9.1.114.3","EM600_3_PhaseCurrentIb","3号电量仪B相电流","4","2","1","3","109",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","21","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["37","9.1.114.3","EM600_3_PhaseCurrentIc","3号电量仪C相电流","4","2","1","3","110",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","21","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["38","9.1.114.3","EM600_3_PhaseActivePowerPa","3号电量仪A相有功功率","3","2","1","3","122",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","KW","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["39","9.1.114.3","EM600_3_PhaseActivePowerPb","3号电量仪B相有功功率","3","2","1","3","123",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","KW","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["40","9.1.114.3","EM600_3_PhaseActivePowerPc","3号电量仪C相有功功率","3","2","1","3","124",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","KW","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["41","9.1.114.3","EM600_3_Frequency","3号电量仪频率","4","2","1","3","113",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","66","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["42","9.1.114.3","EM600_3_Netstatus","3号电量仪通信","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
["43","9.1.114.4","EM600_4_PhaseVoltageUa","4号电量仪A相电压","4","2","1","3","104",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["44","9.1.114.4","EM600_4_PhaseVoltageUb","4号电量仪B相电压","4","2","1","3","105",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["45","9.1.114.4","EM600_4_PhaseVoltageUc","4号电量仪C相电压","4","2","1","3","106",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["46","9.1.114.4","EM600_4_LineVoltageUca","4号电量仪A线电压","4","2","1","3","100",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["47","9.1.114.4","EM600_4_LineVoltageUab","4号电量仪B线电压","4","2","1","3","101",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["48","9.1.114.4","EM600_4_LineVoltageUbc","4号电量仪C线电压","4","2","1","3","102",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["49","9.1.114.4","EM600_4_PhaseCurrentIa","4号电量仪A相电流","4","2","1","3","108",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","21","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["50","9.1.114.4","EM600_4_PhaseCurrentIb","4号电量仪B相电流","4","2","1","3","109",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","21","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["51","9.1.114.4","EM600_4_PhaseCurrentIc","4号电量仪C相电流","4","2","1","3","110",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","21","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["52","9.1.114.4","EM600_4_PhaseActivePowerPa","4号电量仪A相有功功率","3","2","1","3","122",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","KW","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["53","9.1.114.4","EM600_4_PhaseActivePowerPb","4号电量仪B相有功功率","3","2","1","3","123",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","KW","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["54","9.1.114.4","EM600_4_PhaseActivePowerPc","4号电量仪C相有功功率","3","2","1","3","124",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","KW","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["55","9.1.114.4","EM600_4_Frequency","4号电量仪频率","4","2","1","3","113",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","66","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["56","9.1.114.4","EM600_4_Netstatus","4号电量仪通信","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
["57","9.1.114.5","EM600_5_PhaseVoltageUa","5号电量仪A相电压","4","2","1","3","104",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["58","9.1.114.5","EM600_5_PhaseVoltageUb","5号电量仪B相电压","4","2","1","3","105",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["59","9.1.114.5","EM600_5_PhaseVoltageUc","5号电量仪C相电压","4","2","1","3","106",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["60","9.1.114.5","EM600_5_LineVoltageUca","5号电量仪A线电压","4","2","1","3","100",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["61","9.1.114.5","EM600_5_LineVoltageUab","5号电量仪B线电压","4","2","1","3","101",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["62","9.1.114.5","EM600_5_LineVoltageUbc","5号电量仪C线电压","4","2","1","3","102",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["63","9.1.114.5","EM600_5_PhaseCurrentIa","5号电量仪A相电流","4","2","1","3","108",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","21","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["64","9.1.114.5","EM600_5_PhaseCurrentIb","5号电量仪B相电流","4","2","1","3","109",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","21","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["65","9.1.114.5","EM600_5_PhaseCurrentIc","5号电量仪C相电流","4","2","1","3","110",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","21","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["66","9.1.114.5","EM600_5_PhaseActivePowerPa","5号电量仪A相有功功率","3","2","1","3","122",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","KW","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["67","9.1.114.5","EM600_5_PhaseActivePowerPb","5号电量仪B相有功功率","3","2","1","3","123",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","KW","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["68","9.1.114.5","EM600_5_PhaseActivePowerPc","5号电量仪C相有功功率","3","2","1","3","124",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","KW","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["69","9.1.114.5","EM600_5_Frequency","5号电量仪频率","4","2","1","3","113",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","66","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["70","9.1.114.5","EM600_5_Netstatus","5号电量仪通信","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
["71","9.1.114.6","EM600_6_PhaseVoltageUa","6号电量仪A相电压","4","2","1","3","104",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["72","9.1.114.6","EM600_6_PhaseVoltageUb","6号电量仪B相电压","4","2","1","3","105",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["73","9.1.114.6","EM600_6_PhaseVoltageUc","6号电量仪C相电压","4","2","1","3","106",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["74","9.1.114.6","EM600_6_LineVoltageUca","6号电量仪A线电压","4","2","1","3","100",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["75","9.1.114.6","EM600_6_LineVoltageUab","6号电量仪B线电压","4","2","1","3","101",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["76","9.1.114.6","EM600_6_LineVoltageUbc","6号电量仪C线电压","4","2","1","3","102",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["77","9.1.114.6","EM600_6_PhaseCurrentIa","6号电量仪A相电流","4","2","1","3","108",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","21","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["78","9.1.114.6","EM600_6_PhaseCurrentIb","6号电量仪B相电流","4","2","1","3","109",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","21","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["79","9.1.114.6","EM600_6_PhaseCurrentIc","6号电量仪C相电流","4","2","1","3","110",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","21","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["80","9.1.114.6","EM600_6_PhaseActivePowerPa","6号电量仪A相有功功率","3","2","1","3","122",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","KW","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["81","9.1.114.6","EM600_6_PhaseActivePowerPb","6号电量仪B相有功功率","3","2","1","3","123",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","KW","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["82","9.1.114.6","EM600_6_PhaseActivePowerPc","6号电量仪C相有功功率","3","2","1","3","124",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","KW","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["83","9.1.114.6","EM600_6_Frequency","6号电量仪频率","4","2","1","3","113",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","66","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["84","9.1.114.6","EM600_6_Netstatus","6号电量仪通信","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]
["85","9.1.114.7","EM600_7_PhaseVoltageUa","7号电量仪A相电压","4","2","1","3","104",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["86","9.1.114.7","EM600_7_PhaseVoltageUb","7号电量仪B相电压","4","2","1","3","105",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["87","9.1.114.7","EM600_7_PhaseVoltageUc","7号电量仪C相电压","4","2","1","3","106",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["88","9.1.114.7","EM600_7_LineVoltageUca","7号电量仪A线电压","4","2","1","3","100",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["89","9.1.114.7","EM600_7_LineVoltageUab","7号电量仪B线电压","4","2","1","3","101",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["90","9.1.114.7","EM600_7_LineVoltageUbc","7号电量仪C线电压","4","2","1","3","102",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","V","300","0.1","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","1000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["91","9.1.114.7","EM600_7_PhaseCurrentIa","7号电量仪A相电流","4","2","1","3","108",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","21","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["92","9.1.114.7","EM600_7_PhaseCurrentIb","7号电量仪B相电流","4","2","1","3","109",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","21","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["93","9.1.114.7","EM600_7_PhaseCurrentIc","7号电量仪C相电流","4","2","1","3","110",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","A","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","21","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["94","9.1.114.7","EM600_7_PhaseActivePowerPa","7号电量仪A相有功功率","3","2","1","3","122",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","KW","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["95","9.1.114.7","EM600_7_PhaseActivePowerPb","7号电量仪B相有功功率","3","2","1","3","123",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","KW","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["96","9.1.114.7","EM600_7_PhaseActivePowerPc","7号电量仪C相有功功率","3","2","1","3","124",null,null,"0","60","720","1",null,null,"5","0","250","0","0","0","0","0","0","KW","300","0.001","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","100000","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["97","9.1.114.7","EM600_7_Frequency","7号电量仪频率","4","2","1","3","113",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0","Hz","300","0.01","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","66","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["98","9.1.114.7","EM600_7_Netstatus","7号电量仪通信","1000","0","0","1","0",null,null,"0","60","720","1",null,null,"0","0","0","0","0","0","0","0","0",null,"300","1.0000000000","3","0","1","1","0","0","0","0","192",null,null,"0","0","0",{"$nulls":10},"0","0","2","0","0","0","0","0","0","0","0","1","0","0","0","0","0","0","0","0","1","1,","断线报警,"]